# Data Acquisition Description - SCADA Infrastructure and Data Logging Architecture

Operational measurements were acquired through the turbine-level Supervisory Control and Data Acquisition (SCADA) system deployed at VV Wind Farms. Each turbine is equipped with an integrated control and monitoring unit that aggregates:

- Meteorological measurements (nacelle-mounted anemometer, wind vane)

- Mechanical subsystem sensors (rotor encoder, torque transducer, pitch encoders)

- Electrical subsystem measurements (generator voltage, current, frequency, power factor)

- Thermal and condition monitoring sensors (gearbox, bearings, converter modules)

- Control and derived parameters (MPPT reference, tip-speed ratio, Cp, control states)

### Measurement Flow

- Sensors → Turbine PLC (Programmable Logic Controller)

- PLC → Turbine Controller (real-time control logic)

- Controller → SCADA Server (via industrial communication protocol, e.g., IEC 61400 compliant interface)

- SCADA Database → Time-series archival system

All signals are timestamped at source and synchronized using plant-level clock synchronization.

## Instrumentation Standards

The monitoring architecture conforms to internationally recognized wind energy measurement standards:

- IEC 61400-12-1 (Power performance measurement)

- Class 0.2S power analyzers for electrical measurements

- Calibrated cup anemometers (±0.1 m/s accuracy)

- Optical shaft encoders for rotor speed

- PT100 RTDs for temperature measurement

Electrical measurements (voltage, current, active/reactive power) are recorded at turbine output terminals prior to grid step-up transformation.

# Sampling Frequency

## Temporal Resolution

- Raw turbine control signals: high-frequency internal sampling (sub-second resolution)

- SCADA archival frequency: 10-minute averaged intervals

Each stored record represents:

Mean value over 600 seconds

This aligns with standard industrial SCADA aggregation practice in utility-scale wind farms.

## Total Records

For 12 months (January–December 2023):

6 samples/hour×24×365=52,560 records per turbine
With 2 turbines:

52,560×2=105,120 total records
Access Authorization Statement

## Data Access and Authorization Statement

The dataset was obtained under a formal industrial-academic collaboration agreement between the research institution and VV Wind Farms. Data access was granted exclusively for academic research purposes under restricted usage conditions.

The agreement permits:

- Use for feature selection and MPPT optimization research

- Statistical analysis and model validation

- Publication of aggregated results

The agreement prohibits:

- Public release of raw operational SCADA logs

- Disclosure of proprietary operational identifiers

- Exposure of site-level grid interconnection parameters

All shared materials (metadata, structural schema, representative samples) comply with confidentiality constraints while preserving scientific transparency.

Upon reasonable request, verification of data authenticity may be facilitated through institutional or authorized representative confirmation.

Physical Explanation of Power–Current Correlation

This is critical for reviewer-level technical validation.

## Electrical Power Equation

For a three-phase wind turbine generator:

P=3⋅V⋅I⋅cos⁡(ϕ)
Where P= Active power (kW), V= Line voltage (V), I= Line current (A), andcos⁡(ϕ)= Power factor

## Interpretation in Wind Turbines

In grid-connected turbines:

- Voltage Vis regulated by grid conditions (approximately constant)

- Power factor is maintained close to unity (0.9–1.0)

Thus:

P∝I
Active power is approximately linearly proportional to generator current when voltage is stable.

## Aerodynamic to Electrical Coupling

Mechanical power captured from wind:

Pmech=12ρACpVw3
Where ρ= Air density, A= Rotor swept area, Cp= Power coefficient, and Vw= Wind speed.

The generator converts mechanical torque to electrical power:

Pelec=T⋅ω
Where T= Generator torque, and ω= Angular velocity.

As wind speed increases:

- Rotor speed increases

- Generator torque increases

- Electrical current increases

- Active power increases

Hence, the observed SCADA correlation between:

- Wind speed ↑

- Rotor speed ↑

- Generator torque ↑

- Line current ↑

- Active power ↑

## Why Correlation is Strong but Not Perfect

The power–current relationship is influenced by:

- Reactive power control

- Converter switching losses

- Grid voltage fluctuations

- Temperature-dependent resistance

- MPPT control adjustments

- Curtailment or derating

Therefore:

P=f(I,V,cos⁡ϕ,control state)
This explains why correlation is strong (>0.9 in stable regimes) but not perfectly deterministic.

The SCADA dataset represents aggregated 10-minute turbine operational measurements acquired through IEC-compliant instrumentation and archived through plant-level SCADA infrastructure. Electrical power output demonstrates strong physical correlation with generator current as dictated by three-phase power equations and aerodynamic torque conversion mechanisms inherent to grid-connected DFIG and SCIG wind turbine systems.